## (0) Impressum
Link: | https://www.sweet-decarb.ch/decarbonization-tools

## (1) HTHP Evaluation Tool
HTHP Evaluation Tool Annex 58 HTHP-CH | [5 empty] | V1.0, 15/9/2025
|  |  | Case study 1 | Case study 2 | Case study 3 | Reference Case
Company |  |  | ELSA | Cremo | Gustav Spiess
Application process | Symbol | Unit | CIP process | Milk drying | Sausage cooking
Heat sink outlet temperature | T_h_out | °C | 148 | 120 | 115 | 120 |  |  |  | 90 | 96 | 102 | 108 | 114 | 120 | 126 | 132 | 138 | 144 | 150
Heat source inlet temperature | T_c_in | °C | 50 | 38 | 50 | 50 |  |  |  | 37.5 | 40 | 42.5 | 45 | 47.5 | 50 | 52.5 | 55 | 57.5 | 60 | 62.5
Temperature lift | dT_lift | K | 98 | 82 | 65 | 70 |  | Temperature lift |  | 52.5 | 56 | 59.5 | 63 | 66.5 | 70 | 73.5 | 77 | 80.5 | 84 | 87.5
Heating capacity | Q_dot_h | kW | 3150 | 940 | 550 | 1000 |  | Heating capacity |  | 750 | 800 | 850 | 900 | 950 | 1000 | 1050 | 1100 | 1150 | 1200 | 1250
--- Fuel prices, CO2 tax, CO2 emission factors---
Fuel price (gas, oil) | c_fuel | CHF/kWh | 0.13 | 0.11 | 0.17 | 0.15 | Enerprice – Erdgaspreise | Fuel price (gas, oil) |  | 0.1125 | 0.12 | 0.1275 | 0.135 | 0.1425 | 0.15 | 0.1575 | 0.165 | 0.1725 | 0.18 | 0.1875
Electricity price | c_el | CHF/kWh | 0.18 | 0.2 | 0.25 | 0.35 | Enerprice – Strompreis | Electricity price |  | 0.2625 | 0.28 | 0.2975 | 0.315 | 0.3325 | 0.35 | 0.3675 | 0.385 | 0.4025 | 0.42 | 0.4375
CO2 tax or subsidies | c_CO2_tax | CHF/tCO2 | 0 | 0 | 0 | 92.5 |  | CO2 tax |  | 69.375 | 74 | 78.625 | 83.25 | 87.875 | 92.5 | 97.125 | 101.75 | 106.375 | 111 | 115.625
CO2 emissions factor electricity | f_CO2_el | kgCO2/kWh | 0.128 | 0.128 | 0.012 | 0.128 | BAFU Website | CO2 emissions factor of electricity |  | 0.096 | 0.1024 | 0.1088 | 0.1152 | 0.1216 | 0.128 | 0.1344 | 0.1408 | 0.1472 | 0.1536 | 0.16
CO2 emissions factor fuel | f_CO2_fuel | kgCO2/kWh | 0.201 | 0.201 | 0.201 | 0.201 | BAFU (2019) | CO2 emissions factor of fuel |  | 0.15075 | 0.1608 | 0.17085 | 0.1809 | 0.19095 | 0.201 | 0.21105 | 0.2211 | 0.23115 | 0.2412 | 0.25125
CO2 emissions ratio el/gas | e_CO2_el/fuel | - | 0.63682 | 0.63682 | 0.059701 | 0.63682
Electricity-to-fuel price ratio | p_el/fuel | - | 1.3846 | 1.8182 | 1.4706 | 2.3333 |  |  |  | 1.75 | 1.8667 | 1.9833 | 2.1 | 2.2167 | 2.3333 | 2.45 | 2.5667 | 2.6833 | 2.8 | 2.9167
--- Other input parameters---
Annual operating time | t | h/a | 7200 | 6400 | 3000 | 6400 |  | Annual operating time |  | 4800 | 5120 | 5440 | 5760 | 6080 | 6400 | 6720 | 7040 | 7360 | 7680 | 8000
Efficiency of fuel boiler | eta_fuel | - | 0.9 | 0.9 | 0.9 | 0.9 |  | Efficiency of fuel boiler |  | 0.675 | 0.72 | 0.765 | 0.81 | 0.855 | 0.9 | 0.945 | 0.99 | 1.035 | 1.08 | 1.125
Maintenance factor (on capital costs) |  | - | 0.04 | 0.04 | 0.04 | 0.04 |  | Maintenance factor |  | 0.03 | 0.032 | 0.034 | 0.036 | 0.038 | 0.04 | 0.042 | 0.044 | 0.046 | 0.048 | 0.05
Cost factor for planning & integration | f_inv_hp | - | 3 | 2 | 2 | 3 |  | Cost factor planning & integration |  | 2.25 | 2.4 | 2.55 | 2.7 | 2.85 | 3 | 3.15 | 3.3 | 3.45 | 3.6 | 3.75
--- Fit curves --- | [7 empty] | Discount rate |  | 0.075 | 0.08 | 0.085 | 0.09 | 0.095 | 0.1 | 0.105 | 0.11 | 0.115 | 0.12 | 0.125
COP (y=52.94x^-0.716) | COP | - | 1.9864 | 2.2568 | 2.6653 | 2.5275
Specific investment costs (y=3157x^-0.322) | c_inv_hp | CHF/kW | 235.9492 | 348.2791 | 413.8832 | 341.4087 |  |  |  | 90: Sensitivity Analysis
--- CO2 emissions reduction & energy savings --- | [9 empty] | -25% | 20% | -15% | -10% | -5% | 0% | 5% | 10% | 15% | 20% | 25%
Annual CO2 emissions reduction | E_CO2_reduction | tCO2/a | 3603.7399 | 1002.3611 | 361.0711 | 1105.2205 |  |  |  | 0.75 | 0.8 | 0.85 | 0.9 | 0.95 | 1 | 1.05 | 1.1 | 1.15 | 1.2 | 1.25
Annual CO2 emissions reduction | E_CO2_reduction | - | 71.15% | 74.6% | 97.98% | 77.32% |  | Temperature lift | 70 | 52.5 | 56 | 59.5 | 63 | 66.5 | 70 | 73.5 | 77 | 80.5 | 84 | 87.5
Annual energy savings | E_savings | MWh/a | 13782.3432 | 4018.724 | 1214.2545 | 4578.9797 |  | PP | 4.2379
Annual energy savings | E_savings | - | 54.69% | 60.12% | 66.23% | 64.39% |  | Heating capacity | 1000 | 750 | 800 | 850 | 900 | 950 | 1000 | 1050 | 1100 | 1150 | 1200 | 1250
--- Economic calculations --- | [7 empty] | PP | 4.2379
Investment costs | C_inv_hp | kCHF | 2229.7203 | 654.7647 | 455.2715 | 1024.2261 |  | Fuel price (gas, oil) | 0.15 | 0.1125 | 0.12 | 0.1275 | 0.135 | 0.1425 | 0.15 | 0.1575 | 0.165 | 0.1725 | 0.18 | 0.1875
Annual fuel cost savings | C_fuel | kCHF/a | 3276 | 735.2889 | 311.6667 | 1066.6667 |  | PP | 4.2379 | bar: 90
Annual electricity costs | C_el | kCHF/a | 2055.1782 | 533.1441 | 154.7697 | 886.246 |  | Electricity price | 0.35 | 0.2625 | 0.28 | 0.2975 | 0.315 | 0.3325 | 0.35 | 0.3675 | 0.385 | 0.4025 | 0.42 | 0.4375
Annual heat pump maintenance costs | C_maintain | kCHF/a | 89.1888 | 26.1906 | 18.2109 | 40.969 |  | PP | 4.2379
Annual CO2 tax compensation or subsidies | C_CO2 | kCHF/a | 0 | 0 | 0 | 102.2329 |  | CO2 tax | 92.5 | 69.375 | 74 | 78.625 | 83.25 | 87.875 | 92.5 | 97.125 | 101.75 | 106.375 | 111 | 115.625
Annual cost savings | C_savings | kCHF/a | 1131.633 | 175.9542 | 138.6861 | 241.6845 |  | PP | 4.2379
--- Payback --- | [7 empty] | CO2 emissions factor of electricity | 0.128 | 0.096 | 0.1024 | 0.1088 | 0.1152 | 0.1216 | 0.128 | 0.1344 | 0.1408 | 0.1472 | 0.1536 | 0.16
Discount rate | i | - | 0.1 | 0.02 | 0.05 | 0.1 |  | PP | 4.2379
Payback period | PP | years | 1.9704 | 3.7212 | 3.2827 | 4.2379 |  | CO2 emissions factor of fuel | 0.201 | 0.15075 | 0.1608 | 0.17085 | 0.1809 | 0.19095 | 0.201 | 0.21105 | 0.2211 | 0.23115 | 0.2412 | 0.25125
Discounted payback period | DPP | years | 2.3024 | 3.9055 | 3.6747 | 5.784 |  | PP | 4.2379 | bar: 90 to 108; 132 to 150
[8 empty] | Annual operating time | 6400 | 4800 | 5120 | 5440 | 5760 | 6080 | 6400 | 6720 | 7040 | 7360 | 7680 | 8000
[8 empty] | PP | 4.2379
Legend: | Formula: |  |  |  | Limits: |  |  | Efficiency of fuel boiler | 0.9 | 0.675 | 0.72 | 0.765 | 0.81 | 0.855 | 0.9 | 0.945 | 0.99 | 1.035 | 1.08 | 1.125
Input parameter | [7 empty] | PP | 4.2379 | bar: 90 to 108; 132 to 150
Variation parameter |  |  |  |  | 20 to 100 K temperature lift |  |  | Maintenance factor | 0.04 | 0.03 | 0.032 | 0.034 | 0.036 | 0.038 | 0.04 | 0.042 | 0.044 | 0.046 | 0.048 | 0.05
Output parameter | [7 empty] | PP | 4.2379
[5 empty] | 0 to 2'500 kW heating capacity |  |  | Cost factor planning & integration | 3 | 2.25 | 2.4 | 2.55 | 2.7 | 2.85 | 3 | 3.15 | 3.3 | 3.45 | 3.6 | 3.75
[8 empty] | PP | 4.2379
[8 empty] | Discount rate | 0.1 | 0.075 | 0.08 | 0.085 | 0.09 | 0.095 | 0.1 | 0.105 | 0.11 | 0.115 | 0.12 | 0.125
[8 empty] | DPP | 5.784
[22 empty] | - | Ref | +
| Operating hours: | [6 empty] | Ref (PP = 4.2 years) | 4.2379 | 90: 1; 138: excluded because out of range | Electricity price | 0.26 | 0.35 | 0.44 | EUR/kWh
| Hours/Day | Days/Week | Weeks | Hours/Year | [16 empty] | Temperature lift | 52.5 | 70 | 87.5 | K
| 24 | 7 | 52 | 8736 | [16 empty] | Cost factor planning & integration | 2.3 | 3 | 3.8 | -
| 24 | 7 | 51 | 8568 | [16 empty] | Efficiency of fuel boiler | 0.86 | 0.9 | 0.95 | -
| 24 | 7 | 50 | 8400 | [16 empty] | CO2 emissions factor of electricity | 0.096 | 0.128 | 0.16 | kgCO2/kWh
| 24 | 6 | 52 | 7488 | [16 empty] | Maintenance factor | 0.03 | 0.04 | 0.05 | -
| 24 | 6 | 51 | 7344 | [16 empty] | Heating capacity | 750 | 1'000 | 1250 | kW
| 24 | 6 | 50 | 7200 | [16 empty] | CO2 tax | 69.4 | 92.5 | 115.6 | EUR/tCO2
| 24 | 5 | 52 | 6240 | [16 empty] | CO2 emissions factor of fuel | 0.191 | 0.201 | 0.211 | kgCO2/kWh
| 24 | 5 | 51 | 6120 | [16 empty] | Annual operating time | 4'800 | 6'400 | 8'000 | h/a
| 24 | 5 | 50 | 6000 | [16 empty] | Fuel price (gas, oil) | 0.11 | 0.15 | 0.19 | EUR/kWh
[21 empty] | Reference Case 2023 (Ref) | - Variation +
1'000 kW, 50 °C/120 °C (Heat source/sink), COP = 2.5
PP = 4.2 years, DPP = 5.8 years
Copy and paste the lines with values to the sensitivity table into the green lines

## (2) Sensitivity Price Ratio
HTHP Evaluation Tool Annex 58 HTHP-CH |  |  | V1.0, 15/9/2025
|  |  | Reference Case |  | Payback period | [5 empty] | Payback period | [5 empty] | Payback period
Company |  |  |  |  | Electricity-to-fuel price ratio | [5 empty] | Electricity-to-fuel price ratio | [5 empty] | Electricity-to-fuel price ratio
Application process | Symbol | Unit |  |  |  | Electricity price | [5 empty] | Temperature lift | [5 empty] | Cost factor for planning & integration
Heat sink outlet temperature | T_h_out | °C | 120 |  | 4.2113 | 0.25 | 0.3 | 0.35 | 0.4 | 0.45 | 4.2113 | 50 | 60 | 70 | 80 | 90 | 4.2113 | 2 | 2.5 | 3 | 3.5 | 4
Heat source inlet temperature | T_c_in | °C | 50 |  | 0.5 | [5 empty] | 0.5 | [5 empty] | 0.5
Temperature lift | dT_lift | K | 70 |  | 0.6 | [5 empty] | 0.6 | [5 empty] | 0.6
Heating capacity | Q_dot_h | kW | 1000 |  | 0.7 | [5 empty] | 0.7 | [5 empty] | 0.7
--- Fuel prices, CO2 tax, CO2 emission factors--- |  |  |  |  | 0.8 | [5 empty] | 0.8 | [5 empty] | 0.8
Fuel price (gas, oil) | c_fuel | CHF/kWh | 0.15021 |  | 0.9 | [5 empty] | 0.9 | [5 empty] | 0.9
Electricity price | c_el | CHF/kWh | 0.35 |  | 1 | [5 empty] | 1 | [5 empty] | 1
CO2 tax | c_CO2_tax | CHF/tCO2 | 92.5 |  | 1.1 | [5 empty] | 1.1 | [5 empty] | 1.1
CO2 emissions factor electricity | f_CO2_el | kgCO2/kWh | 0.128 | BAFU Website | 1.2 | [5 empty] | 1.2 | [5 empty] | 1.2
CO2 emissions factor fuel | f_CO2_fuel | kgCO2/kWh | 0.201 | BAFU (2019) | 1.3 | [5 empty] | 1.3 | [5 empty] | 1.3
CO2 emissions ratio el/gas | e_CO2_el/fuel | - | 0.63682 |  | 1.4 | [5 empty] | 1.4 | [5 empty] | 1.4
Electricity-to-fuel price ratio | p_el/fuel | - | 2.33 |  | 1.5 | [5 empty] | 1.5 | [5 empty] | 1.5
--- Other input parameters--- |  |  |  |  | 1.6 | [5 empty] | 1.6 | [5 empty] | 1.6
Annual operating time | t | h/a | 6400 |  | 1.7 | [5 empty] | 1.7 | [5 empty] | 1.7
Efficiency of fuel boiler | eta_fuel | - | 0.9 |  | 1.8 | [5 empty] | 1.8 | [5 empty] | 1.8
Maintenance factor (on capital costs) |  | - | 0.04 |  | 1.9 | [5 empty] | 1.9 | [5 empty] | 1.9
Cost factor for planning & integration | f_inv_hp | - | 3 |  | 2 | [5 empty] | 2 | [5 empty] | 2
--- Fit curves --- |  |  |  |  | 2.1 | [5 empty] | 2.1 | [5 empty] | 2.1
COP (y=52.94x^-0.716) | COP | - | 2.5275 |  | 2.2 | [5 empty] | 2.2 | [5 empty] | 2.2
Specific investment costs (y=3157x^-0.322) | c_inv_hp | CHF/kW | 341.4087 |  | 2.3 | [5 empty] | 2.3 | [5 empty] | 2.3
--- CO2 emissions reduction & energy savings --- |  |  |  |  | 2.4 | [5 empty] | 2.4 | [5 empty] | 2.4
Annual CO2 emissions reduction | E_CO2_reduction | tCO2/a | 1105.2205 |  | 2.5 | [5 empty] | 2.5 | [5 empty] | 2.5
Annual CO2 emissions reduction | E_CO2_reduction | - | 77.32% |  | 2.6 | [5 empty] | 2.6 | [5 empty] | 2.6
Annual energy savings | E_savings | MWh/a | 4578.9797 |  | 2.7 | [5 empty] | 2.7 | [5 empty] | 2.7
Annual energy savings | E_savings | - | 64.39% |  | 2.8 | [5 empty] | 2.8 | [5 empty] | 2.8
--- Economic calculations --- |  |  |  |  | 2.9 | [5 empty] | 2.9 | [5 empty] | 2.9
Investment costs | C_inv_hp | kCHF | 1024.2261
Annual fuel cost savings | C_fuel | kCHF/a | 1068.1927
Annual electricity costs | C_el | kCHF/a | 886.246
Annual heat pump maintenance costs | C_maintain | kCHF/a | 40.969
Annual CO2 tax compensation | C_CO2 | kCHF/a | 102.2329
Annual cost savings | C_savings | kCHF/a | 243.2105
--- Payback ---
Discount rate | i | - | 0.1
Payback period | PP | years | 4.2113
Discounted payback period | DPP | years | 5.7357
Legend: | Formula: |  |  | Limits:
Input parameter
Variation parameter |  |  |  | 20 to 100 K temperature lift
Output parameter
0 to 2'500 kW heating capacity